###### Andes UNDERGROUND LABORATORY

Design guidelines

Minusio, May 2018

6198.1-R-01

Basic Engineering Blueprint

DRAFT

| 0 | 15.05.2018 | Gub | … |
| --- | --- | --- | --- |
| Version | Date | Written | Verified |

INDEX

1.	IntrodUCTION	1

1.1	Object	1

1.2 Purpose and scope of the document	1

2.	Bases AND BACKGROUND	3

2.1	ANDES Laboratory Documents	3

2.2	Documents of the Túnel de Agua Negra (TAN)	3

3.	NormS AND DIRECTIVES	4

3.1	Civil Works	4

3.2	Electromechanical instalations and ventilation	4

4.	GENERAL OBJECTIVES OF UTILIZATION	5

4.1	Purpose and use of the Laboratory	5

4.2	Lifetime	5

5.	LABORATORY REQUIREMENTS	7

5.1	Rock cover and location	7

5.2	Access and exit	7

5.3	Internal transit and parking	7

5.4	Coating concept	7

5.5	Waterproof concept	8

5.6	Sewer system and drainage 	8

5.7	Electricity supply	8

5.8	Water supply	8

5.9	External telecommunication connections	8

5.10	Possible future expansion	9

5.11	Laboratory spaces	9

5.12	Ventilation	12

5.13	Air conditioning	12

5.14	Lighting	12

5.15	Surveillance	13

5.16	Security	13

5.17	Communication	13

5.18	Energy and wiring network	13

5.19	Compressed air	14

5.20	Sanitary facilities	14

5.21	Doors and gates	15

5.22	Bridge cranes and lifting systems	15

5.23	Geoscience sector	15

6.	ENVIRONMENT AND EXTERNAL REQUIREMENTS	19

6.1	Environment	19

6.2	Safety and functionality of the Túnel de Agua Negra	19

7.	RiSKS	20

7.1	Geological risk	20

7.2	Earthquake	20

7.3	Risks from the scientific experiments	21

7.4	Accepted risks	21

8.	AGREEMENT	22

# IntroducTION

## 1.1   Object

The ANDES Laboratory (Agua Negra Deep Experiment Site) is an underground laboratory whose construction is foreseen during construction of the Túnel de Agua Negra (TAN) road of international interconnection between Argentina and Chile (see Figure 1). Once built, it will be the first and only underground laboratory in the Southern Hemisphere. Thanks to its high rock cover, its spaces will be protected from cosmic radiation and will offer the ideal conditions to carry out numerous scientific experiments on different specific topics, both Latin American and international.

Brasil

Túnel Agua Negra

ANDESLaboratory

Figure 1: Project location

## Purpose and scope of the document

This report defines the design guidelines for the development of the ANDES Laboratory project and pursues the following objectives:

- Summarize the bases and background of the project,

- Define and agree on the Laboratory requirements with regard to location, coverage, dimensions, access, equipment, connections, etc.

- Identify the main risks,

- Serve as an exchange document between Project Engineer and Client during the Basic Design Engineering (IBA) phase,

- Define the guidelines for the bidding phase (DTL) and for the development of the executive project of the contractor company responsible for carrying out the work.

This report compiles with the general requirements of the Laboratory so that it becomes accessible, habitable, safe, connected, and adequately supplied with electricity, water, and compressed air. The specific requirements, derived from the future scientific experiments that will be carried out inside it, are not included in this report and should be treated together with the definition of the experiments and secured by additional and / or temporary installations.

In the same way, the present report does not include the requirements of technical and housing furniture (computers, chairs, desks, tables, kitchen, beds, showers, cabinets, etc.) for the conditioning of the Laboratory premises.

# Bases and background

## 2.1   ANDES Laboratory Documents

The antecedents considered in the elaboration of the Basic Engineering of Preliminary Project (IBA) and of the Technical Documentation of Bidding (DTL) are the following:

[1] Civil Works of the ANDES Laboratory in the Agua Negra Tunnel, document and plans,

[2] Assessment of the Civil Plan for the Andes Lab, Tony Noble, Queen's University, Canada, 02.2014,

[3] Responses prepared by the coordination of the ANDES project to the Memo de Lombardi SA LO/28.10.2014, Ref: INF / 14-012, Bariloche, Argentina 24.11.2014,

[4] New Conceptual Study of the ANDES Underground Laboratory, 6198.0-R-01 - Technical Report, Lombardi SA, Minusio, Switzerland, 16.01.2015,

[5] Considerations for a geophysical section of the ANDES laboratory, A. Rietbrock& T. Forbriger, Black Forest Observatory (BFO), Geophysical Institute Karlsruhe Institute of Technology (KIT), Germany, 17.07.2017,

[6] Document "Space Biological Investigations of Dr. L. Mongiat, of the 29.08.2017,

[7] Responses to the Lombardi SA document "6198.1-Memo electromechanical installations", H. Asorey, X. Bertou, M. Gómez Berisso, Rev. 1, February 2018,

[8] Document "Modifications proposed to the New Conceptual Study of the underground laboratory ANDES", Coordination Committee ANDES, 25.03.2018

[9] Meeting minutes "IBA and DTL of the ANDES Laboratory" of 11.04.2018 in Buenos Aires - Casa de San Juan, Argentina.

[10] Technical ANDES Note TAN-2018-002 "Muon flux estimation at the ANDES deep underground laboratory, Xavier Bertou, Bariloche Atomic Center, Argentina, 07.05.2018

They are available in http://andeslab.org/iba/.

## 2.2 Documents of the Túnel de Agua Negra (TAN)

The following documents of the TAN project are also considered:

[11] Túnel de Agua Negra of international interconnection between Argentina and Chile, Reports and Plans of the dossier of the Basic Engineering of Preliminary Project (IBA), Lombardi SA, Minusio, Switzerland, 20.10.2014,

[12] Túnel de Agua Negra of international interconnection between Argentina and Chile, dossier Technical Documentation of Tendering (DTL), Lombardi SA, Minusio, Switzerland, 20.10.2014,

# Norms and directives

## 3.1   Civil Works

The following normative table is considered in the elaboration of the project:

For the requirements corresponding to the verification methodologies of the structural elements, reference has been made to the Eurocodes and in particular:

- EN 1992-1-1: 2005 - Part 1: 1 - Eurocode 2: design of concrete structures.

- EN 1997-1: 2005 - Part 1 - Eurocode 7: geotechnical design.

For the definition of the reference environmental conditions and for the definition of the characteristics of concrete, reference has been made to the European standard:

- EN 206 Concrete: 2006 - Part 1: Specification, performance, production and conformity

For the definition of the minimum characteristics of metallic fibers for the reinforcement of concrete, reference has been made to the European standard:

- EN 14889-1 - Fibers for concrete. Part 1: Steel fibers - Definitions, specifications and conformity.

For the definition of the fire safety of the coating structures of the underground works, reference has been made to the guidelines of the Austrian standard:

- Richtlinienfür das EntwerfenvonBahnanlagenanHochleistungsstrecken - Anlage 4 - BaulicherBrandschutz - Objektschutz - in unterirdischenVerkehrsbautenvonEisenbahnHochleistungsstrecken.

To Be Completed (TBC)…

## Electromechanical instalations and ventilations

To Be Designed (TBD)

# GENERAL OBJECTIVES OF UTILIZATION

## 4.1   Purpose and Use of the Laboratory

The ANDES Laboratory project aims to benefit from the construction of the Agua Negra tunnel, which will join the 4th region of Chile with the Argentine province of San Juan, in order to reach a region inside the mountain range with large overburden. In there, various caverns will be built, protected from the cosmic radiation, in order to run various scientific experiments on different scientific topics, among which:

- Detection and understanding of the Neutrino nature

- Search for Dark Matter

- Geophysics and tectonic plate studies

- Biology and radiation damage studies

- Nuclear astrophysics and its relation to fusion

- Low radiation measurement with many areas of application

The creation of this laboratory will allow furthermore an effective regional and global integration, significantly contributing to the progress of science, the formation of highly qualified human resources, and the development of new technologies, promoting cooperation both among Latin-American countries and with groups and countries of the whole world.

## 4.2   Lifetime

The lifetime is the period during which the security and functional efficiency of some part of the civil work is assured though maintenance but without renewal.

Normally the Laboratory will have the same lifetime as the Agua Negra tunnel. In the following table the lifetimes of different elements of the laboratory are listed:

| Civil work part / element | Lifetime |
| --- | --- |
| Civil work |  |
| Shotcrete coating | 60 years |
| Waterproofing | 100 years |
| Formwork covering and concrete internal structure | 100 years |
| Drains, ducts, and inspection chambers | 60 years |
| Water ducts | 60 years |
| Cable ducts | 60 years |
| Electromechanical installations |  |
| Transformers | 40 years |
| Air conditioning and ventilation equipments | 30 years |
| Lightning equipment | 20 years |
| Emergency system | 15 years |
| Safety and communication system | 15 years |
| Doors and gates | 10 years |

Table 1: Lifetime definitions

# LABORatory requirements

## 5.1   Rock cover and Location

The rock overburden of the Laboratory has to be maximized. A minimum of 1,500m of overburden is needed to allow third generation dark matter experiments to be run in the Laboratory. Having more than 1,700m is considered very convenient.

In addition, the muon flux as examined in [10], has to be considered for the selection of the location.

## 5.2   Access and exit

The access and exit from/to the Laboratory should only be possible for authorized personal through a security gate located with an emergency parking area of the Agua Negra tunnel.

The transit for vehicles should be of 3.5m width and 4.5m height and the area should allow the entry, maneuver and exit of a low truck with a 24feet container.

## 5.3   Internal transit and parking

The internal connection galleries and internal gates of the laboratory should allow transit of vehicles of 3.5m width and 4.5m height.

Except in the access and exit zone of the Laboratory, internal combustion engine vehicles will only be allowed to load or unload equipment and material to build and equip experiments. All normal operation vehicles in the Laboratory will be electric.

In the access and exit zone of the Laboratory an area sufficient for the parking of 10 vehicles is needed.

## 5.4   Coating concept

Low radiation shotcrete is foreseen as coating concept.

In case of high radon emanation from the rocks, the internal surfaces of the coating could be treated with a product based on resin (like MineGuard) that would reduce radon permeability, allowing reducing the ventilation needs.

Extra requisites are detailed in the tables of Chapter 5.11.

## 5.5   Waterproof concept

Considering the coating foreseen, no systematic waterproofing system will be implemented for the Laboratory. Eventual water leaks will be taken to the floor through Delta-drain type membranes covered by shotcrete. The concept considers humid zones on walls as acceptable, but water drop in the cavern is not and should be controlled.

Extra requisites are detailed in the tables of Chapter 5.11.

## 5.6   Sewer system and drainage

The sewer system and drainage concept for the laboratory is a recollection system that collects and extracts water from the mountain and used water from the Laboratory in separate ways.

Water filtrating from the mountain and collected by the waterproofing system will be collected and brought to the tunnel to go to the Chilean portal together from the mountain water of the Agua Negra tunnel.

Other used liquids from the Laboratory, potentially loaded with contaminated products, will be stored in tanks and evacuated by cistern trucks. The tanks will have a minimum capacity of 20 m3 and will be made of stainless steel SAE 316L (UNS S31603, ISO 3506 A4), designed according to the rules of ASME Sec. VIII Div. 2.

## 5.7   Electricity supply

For the Laboratory operation, an electric connection with a maximum power of 2 MW is considered.

## 5.8   Water supply

For the total internal use of the Laboratory (experiments and Laboratory personal), a water connection insuring a guaranteed flux of 3-4 l/s with a typical pressure of 2 bar is considered.

This water should comply with the consumable water requirements of the Argentine regulatory code “Agua Potable de Suministro Público” (Art. 982), with the exception of its hardness that should be lower to 200 mg/l of equivalent CaCO3 in order to avoid deposits in pipes, cryogenerators or cooling systems.

## 5.9   External communication connections

The external telecommunication system of the Laboratory will have the following connections:

- One connection with monomode fibers to both portals of the tunnel (Argentina and Chile), for the transition of data and calibration of the Laboratory equipments

- 2 copper lines, one to each country, for an emergency phone system

- A connection to the tunnel communication system, ensuring at all times communication and coordination among the Laboratory and the Agua Negra tunnel

## 5.10   Possible future expansion

The Project does not consider a possible future expansion of the laboratory.

## 5.11   Laboratory spaces

The main specific characteristics of the Laboratory spaces are detailed in the following tables:

| Main cavern |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Main experimental hall |
| Dimensions | Internal free space of 21 m width, 23 m tall and 42 m long |
| Access and Location | Access from the internal connection gallery of the Laboratory |
| Equipments | 40 tons main crane, with the main beam curved to ensure at least 21m equipment to be installed at the center of the cavern. |
| Special requirements | 500 m3 retention pool to keep eventual liquid leaks. Cable gutters on the deck. |

Table 2: Main cavern requirements

| Main pit |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space for large size experiment |
| Dimensions | 30 m internal useful diameter, total height of 38 m |
| Access and Location | Top level access: from the internal connection gallery of the Laboratory Bottom level access: from the bottom pit access gallery |
| Equipments | 40 tons central crane designed to lift either from the top or bottom access and locate equipment in any position within the pit for installation |
| Special requirements | The pit coating will have to be waterproof to allow its filling with liquids (water or other) for the experiments. |

Table 3: Main pit requirements

| Secondary cavern |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space for smaller size experiments, office and secondary installations |
| Dimensions | Free internal space of 16 m width, 14 m tall and 30 m long |
| Access and Location | Access from the internal connection gallery of the Laboratory |
| Equipments | 40 tons main crane, with the main beam curved to ensure at least 12m equipment to be installed at the center of the cavern. |

Table 4: Secondary cavern requirements

| Isolated experimental room |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space for isolated experiments |
| Dimensions | Free internal space of 10 m width, 5 m tall and 30 m long |
| Access and Location | Access from the gallery to the bottom of the main pit |
| Special requirements | The long dimension must look towards the mountain rock |

Table 5: Requirements for the isolated experimental room

| Biology laboratory |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space for biology experiments |
| Dimensions | Free internal space of 9 m width, 3.5 m tall and 16 m long Total surface about 136 m2 |
| Access and Location | Access from the internal connection gallery of the Laboratory |
| Equipments | Single-phase electrical installation, Water and drain connection Prepared for a chemical fume extraction system Prepared for ventilated racks for animal keeping |

Table 6: Biology laboratory requirements

| Emergency room - office |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space for offices, lunch, meeting room, rest area and medical attention. Data processing and storage center, communication center |
| Dimensions | Free internal space of 10 m width, 8 m tall and 10 m long |
| Access and Location | Independent and safe access. Located close to the Laboratory exits |
| Equipments | Single-phase electric installation, Water and drain connection, Telecommunication connection |

Table 7: Emergency room requirements

| Workshop |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space for noisy installations or equipment needing frequent maintenance (transformers, air compressors, supplies, etc.). Mechanical workshop for soldering or similar activities. |
| Dimensions | Depending on the needs. |
| Access and Location | Located outside of the sensitive area of the Laboratory. Easy access. |

Table 8: Workshop requirements

| Clean room 1 and clean room 2 |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space for measurements in very clean conditions |
| Dimensions | 2 separate rooms with internal free space of 10m wide, 8m high and 10m long each |
| Access | Access from the internal connection gallery of the Laboratory. The accesses will have a double electronic management door. The halls will be surrounded by a technical hall ISO Class 7 or Federal Standard Class 10000. |
| Equipments | Safety and cleaning accessories |
| Specific requirements | Clean rooms must comply with ISO Class6 or Federal Standard Class 1000 with positive pressure. The cavern should provide a waterproofing system and an internal cast-in-place concrete lining. |

Table 9: Definition of the requirements of clean rooms 1 and 2

| Room of ventilation and air conditioning |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Technical space for ventilation equipment and air conditioning, including distribution in the Laboratory |
| Dimensions | According to space requirements |
| Access and Location | Location easily accessible and connected to the ventilation channels and to the fresh air duct from the surface |

Table 10: Requirement definitions of the ventilation and air conditioning room.

| Room for the treatment and retention of water |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Technical space for the hydraulic installations of the Laboratory, retention tank and others. |
| Dimensions | According to space requirements |
| Access and Location | External location to the sensitive area of the Laboratory, easily accessible |

Table 11: Definition of the room for the treatment and retention of waters.

## 5.12   Ventilation

The laboratory ventilation concept should consider the following points:

• Ventilation shall ensure that the Laboratory meets the requirements of a clean room according to ISO 146441-1 Class 8 or Federal Standard Class 100000.

• The ventilation must be dimensioned in such a way that the minimum required value of a replacement of the total volume of laboratory air per hour is ensured.

• Radon levels in the Laboratory should be less than 15 Bq / m3 (ideal case) or 150 Bq / m3 (minimum requirement).

• The system must provide an evacuation system for possible toxic gases from the Laboratory. The scenario of a sudden evaporation of a large amount of cryogenic liquids should also be considered.

• In the event of a fire in the Laboratory, the ventilation system must ensure control of the smoke and allow the escape of personnel

For the special requirements of the geophysical sector see Chapter 5.23.

## 5.13   Air conditioning

The air conditioning of the Laboratory must ensure the following conditions:

• Internal temperature of 20-22 ° C,

• Relative humidity of 45-55%,

• Conditioning of the electrical conductivity of the air.

For the evacuation of heat generated by high energy consumption experiments, a heat extraction system is required from the main well.

The entire laboratory must comply with ISO 146441-1 Class 8 or Federal Standard Class 100000. For the additional requirements of clean rooms see Table 9.

For the special requirements of the geophysical sector see chapter 5.23.

## 5.14    llumination

In the caverns destined to the experiments as well as offices and laboratories a diffuse and uniform illumination of 200-400 lux should be foreseen [specify value, proposal LoSA: 100 lux in the zones of transit and corridors and 200-400 lux in the laboratories], according to the guidelines of the IRAM standard AADL J 20-06.

Emergency lighting of escape routes is provided.

Temporary additional lighting requirements will be ensured by means of spot light installations.

## 5.15   Surveillance

The surveillance system must meet the following requirements:

• All laboratory spaces should be provided with local alarms and remote monitoring of low oxygen concentration and high concentrations of radon and carbon monoxide.

• Access doors to scientific and auxiliary facilities should have portable ionizing radiation monitoring systems.

• All accesses and internal spaces of the Laboratory must be monitored through a system of IP network cameras.

• Installation of an alarm system that allows alarms for the different types of risks that could arise in the Laboratory and its facilities. The system must be connected to the security system of the TAN.

• All accesses and internal spaces of the Laboratory should be monitored through a fire detection system.

## 5.16   Safety

In the concept of laboratory safety, the following points should be considered:

• An adequate escape route must ensure at all times the escape of Laboratory personnel to a safe place, whether in the event of an accident in the Laboratory, fire or accident in the adjacent tunnel.

• The Laboratory will be equipped with an anti-fire network connected to the TAN network.

• The Laboratory is not considered an ATEX zone. However, it is recommended to consider the guidelines of the ATEX137 standard.

The specific safety requirements resulting from future scientific experiments that will be carried out in the Laboratory should be considered in the planning of the latter and may require adaptations of the Laboratory's safety concept.

## 5.17   Communications

The Laboratory must have all wired areas for Internet 10 Gb / s (cat 7), on which VoIP phones will be installed. A speaker system for announcements must also be present.

## 5.18   Energy and wiring network

The distribution of electrical energy in the Laboratory must meet the following requirements:

• Three-phase power distribution of 380 V, single-phase of 220 V, three-phase of 190 V and single-phase of 110 V.

• The installed power must not be less than 3 kW / m2 [only in operational zones? Indicate total installed power requirement]

• Installation of boards or access points to these power supplies every 5 m.

• Suitable boards must be provided every 20 m for the distribution of power, with a capacity of not lower than 20 kW. These boards are to be in charge of cutting/controlling the stabilized and uninterrupted lines over its coverage area.

• Installation of at least two independent lines: a power line that includes the three-phase and single-phase power distributions (approximately 1.5 kW/m2), a stabilized line for single-phase distribution (approximately 0.75 kW/m2), and an uninterrupted line for only single-phase distributions (approximately 0.75 kW/m2).

• Installation of panels and gutters with modular design.

• Two independent grounding installations are provided. One for general use of electrical installations and another one for electronic use of less than 2 Ohms.

• The autonomy time of the UPS must be longer than the ignition time and transients of the backup system generators that supply stabilized and uninterrupted lines.

• To recharge the electric vehicles planned for the internal traffic of the laboratory, charging stations should be sized, properly distributed in the caverns. The charging stations will be multimode according to the IEC62196 standard or higher.

## 5.19   Compressed air

In the Laboratory, a compressed air distribution network must be installed that meets the following requirements:

• Working pressure of 3-5 bar,

• Working flow 0.05 liters/minute per m2 of laboratory,

• Autonomy without electrical power of 10 minutes,

• The air must be provided free of oil and particulate. Installation of general and individual filters in the connectors must be foreseen,

• General cut-off key and pressure gauges in the vicinity of the electrical switchgear panels serving the same area of the compressed air service,

• Cutting valve with two quick-coupling connectors located on the perimeter every 10 m.

## 5.20   Sanitation

The Laboratory provides for the installation of toilets and showers for the staff. The wastewater will be retained in tanks and evacuated by tank trucks.

## 5.21   Doors and gates

The doors and gates of the Laboratory shall ensure the separations between the different parts of the Laboratory and the division between the Tunnel and the Laboratory.

The following points should be considered:

• Pedestrian doors shall have a minimum free opening of 0.90 m in width and 2.10 m in height,

• Vehicle doors shall have a minimum free opening of 3.50 m in width and 4.50 m in height,

• The minimum fire resistance is of type FR60,

• The opening and closing of the access and exit gates to/from the Tunnel must be controlled remotely from the Laboratory and from the Tunnel control center,

• The access door to the bottom of the main well must be dimensioned to withstand the pressure in case of filling the water well for future experiments.

## 5.22   Bridge cranes and lifting systems

The main spaces of the Laboratories will be equipped with overhead cranes and other lifting devices detailed in the tables of the Chapter 5.11. In general, in the spaces of the Laboratory, there should be installed fixing points every 5 m in the ridges, dimensioned for loads of 5,000 kg.

At the entrances, lifting mechanisms must be designed for loading and unloading 40-foot shipping containers, coordinated with the lifting devices installed in the respective spaces of the Laboratory.

## 5.23   Geoscience sector

Within the ANDES Laboratory, a specific sector is envisaged for experiments and measurements in the field of geoscience. This sector consists of a tunnel as far as possible from the TAN that allows access to some rooms and spaces for the installation of instruments. The requirements of these spaces differ in part from what was foreseen for the rest of the Laboratory and are summarized in the following tables (see also document [5]):

| Deposit (A) |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Deposit for instruments or materials |
| Dimensions | Internal free space 6.5 m wide, 4 m high and 6.5 m long |
| Access | Direct pedestrian access from the internal connection gallery of the Laboratory |

Table 12: Definition of the deposit requirements of the geoscience sector

| Control room (B) |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space with control screens, storage center and data processing. Small mechanical and electronic workshop. |
| Dimensions | Internal free space 6.5 m wide, 4 m high and 6.5 m long |
| Access | Direct pedestrian access from the internal connection gallery of the Laboratory |

Table 13: Definition of the requirements of the control room of the geophysical sector

| Superconducting Gravimeter Compressor Room (C) |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Space for the installation of the compressor dedicated to the superconducting gravimeter. |
| Dimensions | Internal free space 6.5 m wide, 4 m high and 6.5 m long. |
| Access | Direct pedestrian access from the internal connection gallery of the Laboratory |
| Specific requirements | The room is connected to the instrument room of the superconducting gravimeter (D) by means of a sealed horizontal perforation that will ensure the connection of the high-pressure ducts. |

Table 14: Definition of the demands of the compressor room of the superconducting gravimeter

| Instrument room of the superconducting gravimeter (D) |  |
| --- | --- |
| Characteristics | Requirements |
| Dimensions | Space for the installation of the superconducting gravimeter, including cryogenic refrigeration system. |
| Access | pedestrian access from the Access Tunnel (E) through an air lock. |
| Specific requirements | Pedestrian access deconditioning of air to maintain a temperature below 35 °C (ideally <28 °C). |

Table 15: Definition of the requirements of the instrument room of the superconducting gravimeter

| Access Tunnel (E) |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Ensures access to rooms and spaces of the geoscience sector ensuring the maximum distance between the TAN and the room for short-period sensors (J). Its volume also ensures the effectiveness of the air-lock system. |
| Dimensions | Gauge for the transit of vehicles of 3.00 m wide by 3.50 m high with a length of approximately 200 m |
| Access | Access from the internal-connection gallery of the Laboratory through an air lock. |
| Specific requirements | In principle no specific requirements on air |

Tabla 16: Definition of access tunnel requirements in the geoscience sector.

| Multiple purpose room (F) |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Independent room for other experiments or temporary installations. |
| Dimensions | Internal free space 6.5 m wide, 4 m high and 6.5 m long. |
| Access | Direct pedestrian access from the Access Tunnel (E) through an air lock. |
| Specific Requirements | In principle no specific requirements on air |

Table 17: Definition of the demands of the room for other experiments

| Room for long period sensors (G) |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Independent room for the installation of long period sensors. |
| Dimensions | Internal free space 6.5 m wide, 4 m high and 6.5 m long. |
| Access | Direct pedestrian access from the Access Tunnel (E) through an air lock. |
| Specific requirements | In principle no specific requirements on air |

Table 18: Definition of the demands long period sensors room.

| Sector for extensometers and long base clinometers (H) |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Spaces for the installation of strain gauges and long base clinometers. |
| Dimensions | System of three arms formed by a section of the Access Tunnel (E) and 2 lateral arms of 30 m in length and 120 degrees of angle. Details according to document [5]. |
| Access | Direct pedestrian access from the Access Tunnel (E) through an air lock. |
| Specific requirements | No specific requirement on air. Installation of a series of extensometers in quasi-vertical perforations from the connection point of the different arms. |

Table 19: Definition of the requirements of the sector for extensometers and long-base clinometers

| Room for short-period sensors (J) |  |
| --- | --- |
| Characteristics | Requirements |
| Purpose | Independent room for the installation of short period sensors. |
| Dimensions | Internal free space 6.5 m wide, 4 m high and 6.5 m long. |
| Access | Direct pedestrian access from the Access Tunnel (E) and the sector for strain gagues and long base clinometers (H) through an air lock. |
| Specific requirements | Should be located as far as possible from the Agua Negra main tunnels and other possible vibration sources from the Laboratory. No specific requirement on air. |

Table 20: Definition of the requirements of the short-period sensors room.

Regarding the geophysical sector, the following general requirements are needed:

- Excluding the depot (A), the control room (B), the superconducting gravimeter compressor room (C), and the superconducting gravimeter instrumentation room (D), an air conditioning system for the geoscience sector is not required. In case of temperatures above 60°C – 70°C could be expected, the need for partial air conditioning of some of those spaces should be evaluated. In strain gauges and long base clinometers room (H), and short period sensors sector (J), any type of air conditioning is excluded.

- The drainage water of the geoscience sector must be drained by gravity using a system based on siphons to avoid water losses in correspondence with the air locks.

- The instruments installed in the geoscience sector need a constant and uninterruptible power supply and must be connected to the rest of the lines of the Laboratory (see Chapter 5.18).

- Bearing in mind the conditioning needs of some rooms, all the geoscience sector must be connected to the Laboratory communications and water networks.

- Considering the requirements to eliminate all sensors interference and to minimize the air conditioning system requirements, the geophysical sector with the exception of the depot (A), control (B), superconducting gravimeter compressor room (C), will not fully comply with the standards of safety and health at work, and should therefore remain closed and inaccessible to the laboratory staff. Personnel access will be possible only with a previous and temporary conditioning of spaces (ventilation, radon, lighting, etc.) or by specific safety personal protective equipment (air supply respirators, heat protection, etc.).

- ENVIRONMENT AND EXTERNAL REQUIREMENTS

  - Environment

The Laboratory should be designed so that its impact on the environment be minimum, both during the construction and the operation phases.

The environmental impact of the Laboratory should be analyzed in the scope of the environmental impact assessment (EA) of the rest of the TAN.

  - Safety and functionality of the Black Water Tunnel

The Laboratory should be designed in such a way that the interference with the TAN be minimal. The following points should be considered:

- The safety of tunnel users must be guaranteed at all times.

- The spaces of the Laboratory must be separated and must remain inaccessible for regular users of the Tunnel.

- Entries to/exits from the Laboratory must be coordinated and controlled by the Tunnel control center that may decide on an eventual moderation of traffic in the Tunnel to facilitate the entry/exit of vehicles to/from the Laboratory (temporary right-side lane closure, total closure of the tunnel, etc.).

- In case of an accident in the Laboratory, the alarm system should alert the Tunnel control center and vice versa.

- The ventilation gallery of the Tunnel can be used for the evacuation of fumes/gases in the event of an event in the Laboratory.

- RISKS

  - Geological risk

Taking into account the rock overburden present in the considered section (up to 1700 m), the geological/geomechanical knowledge of the sector is limited and is essentially based on surface mappings and on bibliographic material collected during the Preliminary Project phase.

Due to this severe lack of knowledge, a continuous monitoring of the excavation front conditions is required, imposing the need of performing drill holes during the excavation phase.

In analogy to the TAN Central de Ventilación Oeste, the feasibility of the Laboratory imposes the existence of, at least, a class III massif according to the classification of Bieniawski (1989). If during the construction phase in the pre-selected sector, class IV or class V massif areas were found, the Laboratory must be relocated.

  - Seism

The project area is characterized as a high seismic risk area. In accordance with the TAN project, the support and coating structures of the underground laboratory design must comply with these requirements depending on these two earthquake types:

- Normal Operation Earthquake (TON, Spanish acronym): the occurrence of this type of events must not compromise the laboratory operability;

- Security Earthquake (TS, Spanish acronym): the occurrence of this type of events could interrupt the operations, or even could require the laboratory evacuation, but should not produce the total collapse of laboratory.

Assuming a service life of 100 years for the laboratory, it has been defined for a probability of exceedance of 50% during the service life for TONs and of 2% for TS during the same period of time.

Table 21 below summarizes the values of return period and requirements for both mentioned earthquakes.

| Earthquake [-] | Probability in exceedance of [%] | Tr [years] | Requirement [-] | Event performance [-] |
| --- | --- | --- | --- | --- |
| TON | 50% | 144 | Minor damage or no damage | Fully operational |
| TS | 2% | 5000 | Some levels of structural damage are accepted, but it must allow the complete Laboratory evacuation. | Collapse prevention |

Table 21: Return period and requirements for the two project considered earthquakes.

  - Scientific experiments risks

Any additional risks caused by the presence and/or operation of scientific experiments should be evaluated during the experiment design phase.

  - Accepted risks

The following events are considered as acceptable risks, and no technical or constructive countermeasure is foreseen to face possible impacts:

- Explosion in the Laboratory

- Explosion in the TAN

- Vehicles crashing on the structures and facilities of the Laboratory

- Sabotage

- War events

- AGREEMENT

This document is the base document for the development of the ANDES Laboratory project in the Preliminary Engineering Basic Design phase (IBA, by its spanish initials) and is confirmed by the following representatives:

| PROJECT ENGINEER: | COMITENT: |
| --- | --- |
| Lombardi SA, Consulting Engineers Ing. Gabriele Gubler Ing. Stefano Pomaro Ing. Alessandro Sofia Ing. Fulvio Besseghini | Dr. Hernán Asorey Dr. Xavier Bertou Dr. William Brooks Dr. Claudio Dib Dr. Alberto Etchegoyen Dr. Mariano Gómez Berisso Ing Julio Ortíz Andino Geol. Gustavo Racioppi Ing. Andrés Zini |